## Slide 1
Sigma-3000 / Sigma-4000
보드 공용화 개발
Creativity & Confidence
www.atikorea.com

## Slide 2
2. Test 항목 - 1) calibration - HF
■ Sigma-3000/4000 Board Function List
 | Sigma-1000 | Sigma-3000/4000 (개발 계획서)
Power | 24V | 24V
Ethernet | - | PC
UART1 | LPC | -
UART2 | Auto validation(Panel PC) | PC
UART3 | PLC | PLC
UART4 | DEBUG | DEBUG
UART5 | RS485 | -
Analog Input (External 16bit ADC) | 1 (0~5V) | 4 (4~20mA)
Analog Output (External 12bit DAC) | 4 (0~5V) | 4 (4~20mA)
Digital Input (NPN) | 8 (0~5V) | 16 (0~24V)
Digital Output | Open Collector | Relay 제어
 | 13 (A/V) 13 (LPC) 1 (LPC Start) | 16
 | General output | 
 | 8 (Stir.) | 
Log | SD Card | 

## Slide 3
Panel mount
Sigma-3000/4000 Board
2. Test 항목 - 1) calibration - HF
■ Sigma-3000/4000 Board Block Diagram
MCU
STM32F407
UART#1
I2C#3
SDIO
EEPROM
SPI#2
UART#2
UART#3
POWER#3
(DC 24V)
24V Out
(PC, FAN)
Buck
(DC 5V)
RS232
(Isolator)
RS232
RS232
(Isolator)
Debug
PLC
Output
(16-Port)
GPIO
Input
(16-Port)
Micro
SD Card
DAC_OD
(4-Port)
SPI Select
(5-Port)
Panel PC
UART#6
RS232
(Isolator)
APM200i
POWER#1
(AC 220V)
POWER#2
DAC 1ch
LTC2630
x4
DAC 1ch
LTC2601 / XTR111
x4
ADC 4ch
AD7682
4~20mA x 4
4~20mA x 4
Analog Output
Analog Input
APM200i
PLC
RS232
RS232
Start signal 4-Port
(Digital Input)
Start signal 4-Port
(Digital Output)
Relay 8-Port
(Digital Output)
Relay 8-Port
(Digital Input)
RS232
(PLC)
Digital
Output
(APM200i)
4-Port
Digital
Input
(PLC)
4-Port
4-20mA
Output
(PLC)
4-Port
4-20mA
Input
(APM200i)
4-Port
3.3V
X 16
X 8
RS232
(APM200i)
X 8
X 8
X 8
Digital
Output
(PLC)
8-Port
Digital
Input
(APM200i)
8-Port
24V
24V
Male
9Pin
Female
9Pin
Male
16Pin
D-Sub
5Pin
Male
9Pin
Female
9Pin
Male
16Pin
D-Sub
5Pin
24V
24V
LDO
(3.3V)

## Slide 4
Sigma-3000/4000 Board
2. Test 항목 - 1) calibration - HF
■ Sigma-3000/4000 Board Block Diagram
MCU
STM32F407
UART#1
SDIO
SPI#2
UART#2
UART#3
24V Out
(PC, FAN)
Buck
(DC 5V)
Output
(16-Port)
GPIO
Input
(16-Port)
Micro
SD Card
UART#6
DAC 1ch
LTC2630
x4
DAC 1ch
LTC2601 / XTR111
x4
ADC 4ch
AD7682
4~20mA x 4
4~20mA x 4
3.3V
X 8
X 8
X 8
X 8
24V
24V
LDO
(3.3V)
RS232
(Isolator)
RS232
(Isolator)
RS232
RS232
(Isolator)